## Announcement:
Differential pressure transmitter P 34

Configurable transmitter for pressure and volume flow for installation in a control cabinet

- For measuring positive or negative pressures, even asymmetrically

- Also for volume / mass flow and flow rate measurements

- With temperature input (optional) and built-in, static pressure sensor for P/T compensated volume flow

- With USB port

- Compact housing for control cabinet with IP 20 for top hat rail mounting, without display

- Measurement ranges from 0..10 Pa to 100 kPa

- Measurement ranges / outputs can be configured

- With 2 relay outputs (optional)

- Inductive measurement cell for highly accurate measurement and temperature stability

- High zero point stability thanks to automatic zero point calibration

- Built-in valve provides a high level of overload protection

- Can be calibrated (ex works and on-site)

- CE, GOST and CSA approved

Technical data

Measurement ranges: 	10/50/100/250/500 Pa, 1/2.5/5/10/20/50/100 kPa
(others available upon request, adjustable measurement ranges for volume flow, mass flow and flow rate)
freely scalable from 10..100 % within a measurement range

Analog outputs: 		0 .. 10 V, 0 .. 20 mA, 4 .. 20 mA

Power supply:		24 VAC/DC ±10%

Contact points: 		2 relays max. 230 VAC, 6 A

Measurement accuracy:	±0.2% FS (for measurement ranges ≤ 25 kPa) or ±0.5% FS

Temperature coefficient span:	max. 0.03%of FS/K

Temperature coefficient zero point:	± 0 % (cyclical/manual zero-point correction)

Max. system pressure/

overload capacity:		400 kPa for measurement ranges ≥ 2.5 kPa

200x for measurement ranges < 2.5 kPa

Medium:		air, all non-aggressive and non-flammable gases

Sensor response time:	25 ms

Step response time (T63)

(Time constant):		25 ms .. 60 s (adjustable)

Rated temperature range:	10°C .. 50°C

Storage temperature:	-10°C .. 70°C

Power consumption:	approx. 6 VA

Weight:		approx. 450 g

Pressure ports:	Hose connector NW 4 / 6 mm,
Push-on elbow connector 3 mm / 4 mm / 6 mm

Housing:		control cabinet ABS housing for top hat rail mounting

Protection class:		IP 20

Dimensions:		125 mm x 108 mm x 35.2 mm

Certificates:		CE / UKCA

Data interface:		USB 2.0 Full-Speed Slave (Mini USB)

Certificates (opt.):		DAkkS calibration certificate, ISO factory calibration certificate

Designation:	Differential pressure transmitter

Type: 	P 34

Manufacturer: 	halstrup-walcher GmbH