## Announcement:
Differential pressure transmitter PS 17

Compact standard transmitter

- Either with one fixed measurement range or  toggling between 4 different measurement ranges (optional)

- Zero point correction and via internal pushbutton  or digital input

- Fine adjustment via internal pushbutton

- Can be calibrated

- Measuring symmetric and asymmetric measurement ranges

- Output signals can be configured using DIP switches

- Conversion into square root signal ad-justable

- Also as 2-wire system or with relay (optional)

- With LCD (optional)

- Top-hat rail mounting and wall surface installation IP 67

- Plug for easy commissioning (optional)

Technical data

Measurement ranges:	50/100/200/500 Pa, 1/2.5/5/10kPa

Outputs: 		0 .. 10 V, 2 .. 10 V, 0 .. 20 mA, 4 .. 20 mA

Power supply:	24 VAC/DC (50/60 Hz, ± 10 % reverse pole protection) 15..32 VDC (two-wire) 24 VDC (with galvanic separation)

LCD: 		3 ½ digit (optional)

Contact points: 	1 relay (exchange contacts) max. 230 V AC, 6 A
(not for two-wire)

Measurement accuracy: 	± 1 % FS ± 1 Pa measurement range ≤ 250 Pa
± 1 % FS ± 0.5 Pa measurement range > 250 Pa

Temperature coefficient span:	0.1 % of max. value / K

Temperature coefficient zero point:	0.1 % of max. value / K

Max. system pressure/

Overload capacity:	± 25 kPa (measurement ranges ≤ 250 Pa)
± 50 kPa (measurement ranges > 250 Pa)

Medium: 		dry air, non-aggressive and non-flammable gases

Sensor response:		25 ms

Step response time (T63)

(Time constant):		25 ms .. 10s (adjustable)

Rated temperature range:	- 10 .. 70 ° C with display: 0 .. 50 ° C

Storage temperature: 	- 10 .. 70 ° C with display: - 5 .. 55 ° C

Power consumption: 	< 1 W (Option Relay: < 4 W)

Weight: 		approx. 200 g

Electrical connection: 	spring-type terminal and cable glands
2 x M 16 or 1 x M20 or M12 plug (optional)

Pressure ports: 		for tubing NW 4 and 6 mm

Protection class: 		IP 67

Housing/ cover: 		ABS, top-hat rail assembly and wall mounting possible

Dimensions: 		103 mm x 78 mm x 65 mm

Certificates: 		CE / UKCA

Optional: 		DAkkS or ISO factory calibration certificate

Designation:	Differential pressure transmitter

Type: 	PS 17

Manufacturer: 	halstrup-walcher GmbH